## CaseLOHS_in
# CaseLOHS — Loss of Heat Sink from full power.
# SG heat removal ramps from 575 MW to 0 over 10-120 s (loss of feedwater).
# Pressurizer absorbs initial expansion, goes solid, PORV lifts at 16500 kPa.
# High-pressure scram at 16550 kPa. Endtime = 500 s after scram.
# Job Control
endtime = 600
rcs_enthalpy_relax_tau_s = 25.0
rcs_enthalpy_relax_intact_only = 1
full_power_flag = 1 # ATWS
pump_flag = 1
pump_scram_trip = 1
sg_table_flag = 1
core_flag = 1
# RCS geometry
R5_lowCV_height = 70 * 0.3048
R5_highCV_height = 7 * 0.3048
R5_area = 33.0 * 0.3048**2
loop_vol_m3 = 5.0
# Pressurizer — initialised at full-power operating level (~85%)
pzr_area = 33.0 * 0.3048**2
pzr_height = 7 * 0.3048
pzr_level_init = 0.85 * 7 * 0.3048
pzr_level_hi = 0.9 * 7 * 0.3048
PORV_setpoint_kPa = 16500.0
PORV_area_m2 = 0.003
PORV_Cd = 0.84
# Accumulator
acc_area = 66.63 * 0.3048**2
acc_length = 10.5 * 0.3048
acc_totvol = acc_area * acc_length
acc_gasvol = acc_totvol - 630.0 * 0.3048**3
acc_narea = 0.032 * 0.3048**2
inflow_info = {'pressure': 600.0*6.895, 'temp': 49.85}
# Initial Conditions — full power operating state
pressure_kPa = 15500.0
pressure_containment = 101.0
temp_core_exit = 312.8
# Reactor power — full power until scram
total_power = 575
Tinf = 365 * 24 * 3600
U239yield = 1.0
fr35 = 0.81
fr38 = 0.13
fr39 = 0.06
Efis = 200
# RPS Trips
trip_P_hi_kPa = 16550.0
trip_P_lo_kPa = 0
trip_power_frac = 1.10
trip_time_s = 1e6
trip_flow_frac = 0
# Simulation flags
F_r = 1.3
F_z = 1.55
# Core heat transfer
k_fuel = 3.0
h_gap = 6000.0
r_fuel_m = 0.00418
rho_fuel = 10400.0
cp_fuel = 330.0
htc_relax = 0.3
# Table header (no power or rho table needed) | Struct Q (MW) | Decay Q (MW) | SG Q (MW) | unused | rho_ext (pcm)
Time (s) | 0 | 0 | 575 | 0 | 0
0 | 0 | 0 | 575 | 0 | 0
0.5 | 0 | 0 | 575 | 0 | 0
1 | 0 | 0 | 575 | 0 | 0
1.5 | 0 | 0 | 575 | 0 | 0
2 | 0 | 0 | 575 | 0 | 0
2.5 | 0 | 0 | 575 | 0 | 0
3 | 0 | 0 | 575 | 0 | 0
3.5 | 0 | 0 | 575 | 0 | 0
4 | 0 | 0 | 575 | 0 | 0
4.5 | 0 | 0 | 575 | 0 | 0
5 | 0 | 0 | 575 | 0 | 0
5.5 | 0 | 0 | 575 | 0 | 0
6 | 0 | 0 | 575 | 0 | 0
6.5 | 0 | 0 | 575 | 0 | 0
7 | 0 | 0 | 575 | 0 | 0
7.5 | 0 | 0 | 575 | 0 | 0
8 | 0 | 0 | 575 | 0 | 0
8.5 | 0 | 0 | 575 | 0 | 0
9 | 0 | 0 | 575 | 0 | 0
9.5 | 0 | 0 | 575 | 0 | 0
10 | 0 | 0 | 572.3864 | 0 | 0
10.5 | 0 | 0 | 569.7727 | 0 | 0
11 | 0 | 0 | 567.1591 | 0 | 0
11.5 | 0 | 0 | 564.5455 | 0 | 0
12 | 0 | 0 | 561.9318 | 0 | 0
12.5 | 0 | 0 | 559.3182 | 0 | 0
13 | 0 | 0 | 556.7045 | 0 | 0
13.5 | 0 | 0 | 554.0909 | 0 | 0
14 | 0 | 0 | 551.4773 | 0 | 0
14.5 | 0 | 0 | 548.8636 | 0 | 0
15 | 0 | 0 | 546.25 | 0 | 0
15.5 | 0 | 0 | 543.6364 | 0 | 0
16 | 0 | 0 | 541.0227 | 0 | 0
16.5 | 0 | 0 | 538.4091 | 0 | 0
17 | 0 | 0 | 535.7955 | 0 | 0
17.5 | 0 | 0 | 533.1818 | 0 | 0
18 | 0 | 0 | 530.5682 | 0 | 0
18.5 | 0 | 0 | 527.9545 | 0 | 0
19 | 0 | 0 | 525.3409 | 0 | 0
19.5 | 0 | 0 | 522.7273 | 0 | 0
20 | 0 | 0 | 520.1136 | 0 | 0
20.5 | 0 | 0 | 517.5 | 0 | 0
21 | 0 | 0 | 514.8864 | 0 | 0
21.5 | 0 | 0 | 512.2727 | 0 | 0
22 | 0 | 0 | 509.6591 | 0 | 0
22.5 | 0 | 0 | 507.0455 | 0 | 0
23 | 0 | 0 | 504.4318 | 0 | 0
23.5 | 0 | 0 | 501.8182 | 0 | 0
24 | 0 | 0 | 499.2045 | 0 | 0
24.5 | 0 | 0 | 496.5909 | 0 | 0
25 | 0 | 0 | 493.9773 | 0 | 0
25.5 | 0 | 0 | 491.3636 | 0 | 0
26 | 0 | 0 | 488.75 | 0 | 0
26.5 | 0 | 0 | 486.1364 | 0 | 0
27 | 0 | 0 | 483.5227 | 0 | 0
27.5 | 0 | 0 | 480.9091 | 0 | 0
28 | 0 | 0 | 478.2955 | 0 | 0
28.5 | 0 | 0 | 475.6818 | 0 | 0
29 | 0 | 0 | 473.0682 | 0 | 0
29.5 | 0 | 0 | 470.4545 | 0 | 0
30 | 0 | 0 | 467.8409 | 0 | 0
30.5 | 0 | 0 | 465.2273 | 0 | 0
31 | 0 | 0 | 462.6136 | 0 | 0
31.5 | 0 | 0 | 460 | 0 | 0
32 | 0 | 0 | 457.3864 | 0 | 0
32.5 | 0 | 0 | 454.7727 | 0 | 0
33 | 0 | 0 | 452.1591 | 0 | 0
33.5 | 0 | 0 | 449.5455 | 0 | 0
34 | 0 | 0 | 446.9318 | 0 | 0
34.5 | 0 | 0 | 444.3182 | 0 | 0
35 | 0 | 0 | 441.7045 | 0 | 0
35.5 | 0 | 0 | 439.0909 | 0 | 0
36 | 0 | 0 | 436.4773 | 0 | 0
36.5 | 0 | 0 | 433.8636 | 0 | 0
37 | 0 | 0 | 431.25 | 0 | 0
37.5 | 0 | 0 | 428.6364 | 0 | 0
38 | 0 | 0 | 426.0227 | 0 | 0
38.5 | 0 | 0 | 423.4091 | 0 | 0
39 | 0 | 0 | 420.7955 | 0 | 0
39.5 | 0 | 0 | 418.1818 | 0 | 0
40 | 0 | 0 | 415.5682 | 0 | 0
40.5 | 0 | 0 | 412.9545 | 0 | 0
41 | 0 | 0 | 410.3409 | 0 | 0
41.5 | 0 | 0 | 407.7273 | 0 | 0
42 | 0 | 0 | 405.1136 | 0 | 0
42.5 | 0 | 0 | 402.5 | 0 | 0
43 | 0 | 0 | 399.8864 | 0 | 0
43.5 | 0 | 0 | 397.2727 | 0 | 0
44 | 0 | 0 | 394.6591 | 0 | 0
44.5 | 0 | 0 | 392.0455 | 0 | 0
45 | 0 | 0 | 389.4318 | 0 | 0
45.5 | 0 | 0 | 386.8182 | 0 | 0
46 | 0 | 0 | 384.2045 | 0 | 0
46.5 | 0 | 0 | 381.5909 | 0 | 0
47 | 0 | 0 | 378.9773 | 0 | 0
47.5 | 0 | 0 | 376.3636 | 0 | 0
48 | 0 | 0 | 373.75 | 0 | 0
48.5 | 0 | 0 | 371.1364 | 0 | 0
49 | 0 | 0 | 368.5227 | 0 | 0
49.5 | 0 | 0 | 365.9091 | 0 | 0
50 | 0 | 0 | 363.2955 | 0 | 0
50.5 | 0 | 0 | 360.6818 | 0 | 0
51 | 0 | 0 | 358.0682 | 0 | 0
51.5 | 0 | 0 | 355.4545 | 0 | 0
52 | 0 | 0 | 352.8409 | 0 | 0
52.5 | 0 | 0 | 350.2273 | 0 | 0
53 | 0 | 0 | 347.6136 | 0 | 0
53.5 | 0 | 0 | 345 | 0 | 0
54 | 0 | 0 | 342.3864 | 0 | 0
54.5 | 0 | 0 | 339.7727 | 0 | 0
55 | 0 | 0 | 337.1591 | 0 | 0
55.5 | 0 | 0 | 334.5455 | 0 | 0
56 | 0 | 0 | 331.9318 | 0 | 0
56.5 | 0 | 0 | 329.3182 | 0 | 0
57 | 0 | 0 | 326.7045 | 0 | 0
57.5 | 0 | 0 | 324.0909 | 0 | 0
58 | 0 | 0 | 321.4773 | 0 | 0
58.5 | 0 | 0 | 318.8636 | 0 | 0
59 | 0 | 0 | 316.25 | 0 | 0
59.5 | 0 | 0 | 313.6364 | 0 | 0
60 | 0 | 0 | 311.0227 | 0 | 0
60.5 | 0 | 0 | 308.4091 | 0 | 0
61 | 0 | 0 | 305.7955 | 0 | 0
61.5 | 0 | 0 | 303.1818 | 0 | 0
62 | 0 | 0 | 300.5682 | 0 | 0
62.5 | 0 | 0 | 297.9545 | 0 | 0
63 | 0 | 0 | 295.3409 | 0 | 0
63.5 | 0 | 0 | 292.7273 | 0 | 0
64 | 0 | 0 | 290.1136 | 0 | 0
64.5 | 0 | 0 | 287.5 | 0 | 0
65 | 0 | 0 | 284.8864 | 0 | 0
65.5 | 0 | 0 | 282.2727 | 0 | 0
66 | 0 | 0 | 279.6591 | 0 | 0
66.5 | 0 | 0 | 277.0455 | 0 | 0
67 | 0 | 0 | 274.4318 | 0 | 0
67.5 | 0 | 0 | 271.8182 | 0 | 0
68 | 0 | 0 | 269.2045 | 0 | 0
68.5 | 0 | 0 | 266.5909 | 0 | 0
69 | 0 | 0 | 263.9773 | 0 | 0
69.5 | 0 | 0 | 261.3636 | 0 | 0
70 | 0 | 0 | 258.75 | 0 | 0
70.5 | 0 | 0 | 256.1364 | 0 | 0
71 | 0 | 0 | 253.5227 | 0 | 0
71.5 | 0 | 0 | 250.9091 | 0 | 0
72 | 0 | 0 | 248.2955 | 0 | 0
72.5 | 0 | 0 | 245.6818 | 0 | 0
73 | 0 | 0 | 243.0682 | 0 | 0
73.5 | 0 | 0 | 240.4545 | 0 | 0
74 | 0 | 0 | 237.8409 | 0 | 0
74.5 | 0 | 0 | 235.2273 | 0 | 0
75 | 0 | 0 | 232.6136 | 0 | 0
75.5 | 0 | 0 | 230 | 0 | 0
76 | 0 | 0 | 227.3864 | 0 | 0
76.5 | 0 | 0 | 224.7727 | 0 | 0
77 | 0 | 0 | 222.1591 | 0 | 0
77.5 | 0 | 0 | 219.5455 | 0 | 0
78 | 0 | 0 | 216.9318 | 0 | 0
78.5 | 0 | 0 | 214.3182 | 0 | 0
79 | 0 | 0 | 211.7045 | 0 | 0
79.5 | 0 | 0 | 209.0909 | 0 | 0
80 | 0 | 0 | 206.4773 | 0 | 0
80.5 | 0 | 0 | 203.8636 | 0 | 0
81 | 0 | 0 | 201.25 | 0 | 0
81.5 | 0 | 0 | 198.6364 | 0 | 0
82 | 0 | 0 | 196.0227 | 0 | 0
82.5 | 0 | 0 | 193.4091 | 0 | 0
83 | 0 | 0 | 190.7955 | 0 | 0
83.5 | 0 | 0 | 188.1818 | 0 | 0
84 | 0 | 0 | 185.5682 | 0 | 0
84.5 | 0 | 0 | 182.9545 | 0 | 0
85 | 0 | 0 | 180.3409 | 0 | 0
85.5 | 0 | 0 | 177.7273 | 0 | 0
86 | 0 | 0 | 175.1136 | 0 | 0
86.5 | 0 | 0 | 172.5 | 0 | 0
87 | 0 | 0 | 169.8864 | 0 | 0
87.5 | 0 | 0 | 167.2727 | 0 | 0
88 | 0 | 0 | 164.6591 | 0 | 0
88.5 | 0 | 0 | 162.0455 | 0 | 0
89 | 0 | 0 | 159.4318 | 0 | 0
89.5 | 0 | 0 | 156.8182 | 0 | 0
90 | 0 | 0 | 154.2045 | 0 | 0
90.5 | 0 | 0 | 151.5909 | 0 | 0
91 | 0 | 0 | 148.9773 | 0 | 0
91.5 | 0 | 0 | 146.3636 | 0 | 0
92 | 0 | 0 | 143.75 | 0 | 0
92.5 | 0 | 0 | 141.1364 | 0 | 0
93 | 0 | 0 | 138.5227 | 0 | 0
93.5 | 0 | 0 | 135.9091 | 0 | 0
94 | 0 | 0 | 133.2955 | 0 | 0
94.5 | 0 | 0 | 130.6818 | 0 | 0
95 | 0 | 0 | 128.0682 | 0 | 0
95.5 | 0 | 0 | 125.4545 | 0 | 0
96 | 0 | 0 | 122.8409 | 0 | 0
96.5 | 0 | 0 | 120.2273 | 0 | 0
97 | 0 | 0 | 117.6136 | 0 | 0
97.5 | 0 | 0 | 115 | 0 | 0
98 | 0 | 0 | 112.3864 | 0 | 0
98.5 | 0 | 0 | 109.7727 | 0 | 0
99 | 0 | 0 | 107.1591 | 0 | 0
99.5 | 0 | 0 | 104.5455 | 0 | 0
100 | 0 | 0 | 101.9318 | 0 | 0
100.5 | 0 | 0 | 99.3182 | 0 | 0
101 | 0 | 0 | 96.7045 | 0 | 0
101.5 | 0 | 0 | 94.0909 | 0 | 0
102 | 0 | 0 | 91.4773 | 0 | 0
102.5 | 0 | 0 | 88.8636 | 0 | 0
103 | 0 | 0 | 86.25 | 0 | 0
103.5 | 0 | 0 | 83.6364 | 0 | 0
104 | 0 | 0 | 81.0227 | 0 | 0
104.5 | 0 | 0 | 78.4091 | 0 | 0
105 | 0 | 0 | 75.7955 | 0 | 0
105.5 | 0 | 0 | 73.1818 | 0 | 0
106 | 0 | 0 | 70.5682 | 0 | 0
106.5 | 0 | 0 | 67.9545 | 0 | 0
107 | 0 | 0 | 65.3409 | 0 | 0
107.5 | 0 | 0 | 62.7273 | 0 | 0
108 | 0 | 0 | 60.1136 | 0 | 0
108.5 | 0 | 0 | 57.5 | 0 | 0
109 | 0 | 0 | 54.8864 | 0 | 0
109.5 | 0 | 0 | 52.2727 | 0 | 0
110 | 0 | 0 | 49.6591 | 0 | 0
110.5 | 0 | 0 | 47.0455 | 0 | 0
111 | 0 | 0 | 44.4318 | 0 | 0
111.5 | 0 | 0 | 41.8182 | 0 | 0
112 | 0 | 0 | 39.2045 | 0 | 0
112.5 | 0 | 0 | 36.5909 | 0 | 0
113 | 0 | 0 | 33.9773 | 0 | 0
113.5 | 0 | 0 | 31.3636 | 0 | 0
114 | 0 | 0 | 28.75 | 0 | 0
114.5 | 0 | 0 | 26.1364 | 0 | 0
115 | 0 | 0 | 23.5227 | 0 | 0
115.5 | 0 | 0 | 20.9091 | 0 | 0
116 | 0 | 0 | 18.2955 | 0 | 0
116.5 | 0 | 0 | 15.6818 | 0 | 0
117 | 0 | 0 | 13.0682 | 0 | 0
117.5 | 0 | 0 | 10.4545 | 0 | 0
118 | 0 | 0 | 7.8409 | 0 | 0
118.5 | 0 | 0 | 5.2273 | 0 | 0
119 | 0 | 0 | 2.6136 | 0 | 0
119.5 | 0 | 0 | 0 | 0 | 0
120 | 0 | 0 | 0 | 0 | 0
120.5 | 0 | 0 | 0 | 0 | 0
121 | 0 | 0 | 0 | 0 | 0
121.5 | 0 | 0 | 0 | 0 | 0
122 | 0 | 0 | 0 | 0 | 0
122.5 | 0 | 0 | 0 | 0 | 0
123 | 0 | 0 | 0 | 0 | 0
123.5 | 0 | 0 | 0 | 0 | 0
124 | 0 | 0 | 0 | 0 | 0
124.5 | 0 | 0 | 0 | 0 | 0
125 | 0 | 0 | 0 | 0 | 0
125.5 | 0 | 0 | 0 | 0 | 0
126 | 0 | 0 | 0 | 0 | 0
126.5 | 0 | 0 | 0 | 0 | 0
127 | 0 | 0 | 0 | 0 | 0
127.5 | 0 | 0 | 0 | 0 | 0
128 | 0 | 0 | 0 | 0 | 0
128.5 | 0 | 0 | 0 | 0 | 0
129 | 0 | 0 | 0 | 0 | 0
129.5 | 0 | 0 | 0 | 0 | 0
130 | 0 | 0 | 0 | 0 | 0
130.5 | 0 | 0 | 0 | 0 | 0
131 | 0 | 0 | 0 | 0 | 0
131.5 | 0 | 0 | 0 | 0 | 0
132 | 0 | 0 | 0 | 0 | 0
132.5 | 0 | 0 | 0 | 0 | 0
133 | 0 | 0 | 0 | 0 | 0
133.5 | 0 | 0 | 0 | 0 | 0
134 | 0 | 0 | 0 | 0 | 0
134.5 | 0 | 0 | 0 | 0 | 0
135 | 0 | 0 | 0 | 0 | 0
135.5 | 0 | 0 | 0 | 0 | 0
136 | 0 | 0 | 0 | 0 | 0
136.5 | 0 | 0 | 0 | 0 | 0
137 | 0 | 0 | 0 | 0 | 0
137.5 | 0 | 0 | 0 | 0 | 0
138 | 0 | 0 | 0 | 0 | 0
138.5 | 0 | 0 | 0 | 0 | 0
139 | 0 | 0 | 0 | 0 | 0
139.5 | 0 | 0 | 0 | 0 | 0
140 | 0 | 0 | 0 | 0 | 0
140.5 | 0 | 0 | 0 | 0 | 0
141 | 0 | 0 | 0 | 0 | 0
141.5 | 0 | 0 | 0 | 0 | 0
142 | 0 | 0 | 0 | 0 | 0
142.5 | 0 | 0 | 0 | 0 | 0
143 | 0 | 0 | 0 | 0 | 0
143.5 | 0 | 0 | 0 | 0 | 0
144 | 0 | 0 | 0 | 0 | 0
144.5 | 0 | 0 | 0 | 0 | 0
145 | 0 | 0 | 0 | 0 | 0
145.5 | 0 | 0 | 0 | 0 | 0
146 | 0 | 0 | 0 | 0 | 0
146.5 | 0 | 0 | 0 | 0 | 0
147 | 0 | 0 | 0 | 0 | 0
147.5 | 0 | 0 | 0 | 0 | 0
148 | 0 | 0 | 0 | 0 | 0
148.5 | 0 | 0 | 0 | 0 | 0
149 | 0 | 0 | 0 | 0 | 0
149.5 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0
150.5 | 0 | 0 | 0 | 0 | 0
151 | 0 | 0 | 0 | 0 | 0
151.5 | 0 | 0 | 0 | 0 | 0
152 | 0 | 0 | 0 | 0 | 0
152.5 | 0 | 0 | 0 | 0 | 0
153 | 0 | 0 | 0 | 0 | 0
153.5 | 0 | 0 | 0 | 0 | 0
154 | 0 | 0 | 0 | 0 | 0
154.5 | 0 | 0 | 0 | 0 | 0
155 | 0 | 0 | 0 | 0 | 0
155.5 | 0 | 0 | 0 | 0 | 0
156 | 0 | 0 | 0 | 0 | 0
156.5 | 0 | 0 | 0 | 0 | 0
157 | 0 | 0 | 0 | 0 | 0
157.5 | 0 | 0 | 0 | 0 | 0
158 | 0 | 0 | 0 | 0 | 0
158.5 | 0 | 0 | 0 | 0 | 0
159 | 0 | 0 | 0 | 0 | 0
159.5 | 0 | 0 | 0 | 0 | 0
160 | 0 | 0 | 0 | 0 | 0
160.5 | 0 | 0 | 0 | 0 | 0
161 | 0 | 0 | 0 | 0 | 0
161.5 | 0 | 0 | 0 | 0 | 0
162 | 0 | 0 | 0 | 0 | 0
162.5 | 0 | 0 | 0 | 0 | 0
163 | 0 | 0 | 0 | 0 | 0
163.5 | 0 | 0 | 0 | 0 | 0
164 | 0 | 0 | 0 | 0 | 0
164.5 | 0 | 0 | 0 | 0 | 0
165 | 0 | 0 | 0 | 0 | 0
165.5 | 0 | 0 | 0 | 0 | 0
166 | 0 | 0 | 0 | 0 | 0
166.5 | 0 | 0 | 0 | 0 | 0
167 | 0 | 0 | 0 | 0 | 0
167.5 | 0 | 0 | 0 | 0 | 0
168 | 0 | 0 | 0 | 0 | 0
168.5 | 0 | 0 | 0 | 0 | 0
169 | 0 | 0 | 0 | 0 | 0
169.5 | 0 | 0 | 0 | 0 | 0
170 | 0 | 0 | 0 | 0 | 0
170.5 | 0 | 0 | 0 | 0 | 0
171 | 0 | 0 | 0 | 0 | 0
171.5 | 0 | 0 | 0 | 0 | 0
172 | 0 | 0 | 0 | 0 | 0
172.5 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0
173.5 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0
174.5 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0
175.5 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0
176.5 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0
177.5 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0
178.5 | 0 | 0 | 0 | 0 | 0
179 | 0 | 0 | 0 | 0 | 0
179.5 | 0 | 0 | 0 | 0 | 0
180 | 0 | 0 | 0 | 0 | 0
180.5 | 0 | 0 | 0 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0
181.5 | 0 | 0 | 0 | 0 | 0
182 | 0 | 0 | 0 | 0 | 0
182.5 | 0 | 0 | 0 | 0 | 0
183 | 0 | 0 | 0 | 0 | 0
183.5 | 0 | 0 | 0 | 0 | 0
184 | 0 | 0 | 0 | 0 | 0
184.5 | 0 | 0 | 0 | 0 | 0
185 | 0 | 0 | 0 | 0 | 0
185.5 | 0 | 0 | 0 | 0 | 0
186 | 0 | 0 | 0 | 0 | 0
186.5 | 0 | 0 | 0 | 0 | 0
187 | 0 | 0 | 0 | 0 | 0
187.5 | 0 | 0 | 0 | 0 | 0
188 | 0 | 0 | 0 | 0 | 0
188.5 | 0 | 0 | 0 | 0 | 0
189 | 0 | 0 | 0 | 0 | 0
189.5 | 0 | 0 | 0 | 0 | 0
190 | 0 | 0 | 0 | 0 | 0
190.5 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0
191.5 | 0 | 0 | 0 | 0 | 0
192 | 0 | 0 | 0 | 0 | 0
192.5 | 0 | 0 | 0 | 0 | 0
193 | 0 | 0 | 0 | 0 | 0
193.5 | 0 | 0 | 0 | 0 | 0
194 | 0 | 0 | 0 | 0 | 0
194.5 | 0 | 0 | 0 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0
195.5 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0
196.5 | 0 | 0 | 0 | 0 | 0
197 | 0 | 0 | 0 | 0 | 0
197.5 | 0 | 0 | 0 | 0 | 0
198 | 0 | 0 | 0 | 0 | 0
198.5 | 0 | 0 | 0 | 0 | 0
199 | 0 | 0 | 0 | 0 | 0
199.5 | 0 | 0 | 0 | 0 | 0
200 | 0 | 0 | 0 | 0 | 0
200.5 | 0 | 0 | 0 | 0 | 0
201 | 0 | 0 | 0 | 0 | 0
201.5 | 0 | 0 | 0 | 0 | 0
202 | 0 | 0 | 0 | 0 | 0
202.5 | 0 | 0 | 0 | 0 | 0
203 | 0 | 0 | 0 | 0 | 0
203.5 | 0 | 0 | 0 | 0 | 0
204 | 0 | 0 | 0 | 0 | 0
204.5 | 0 | 0 | 0 | 0 | 0
205 | 0 | 0 | 0 | 0 | 0
205.5 | 0 | 0 | 0 | 0 | 0
206 | 0 | 0 | 0 | 0 | 0
206.5 | 0 | 0 | 0 | 0 | 0
207 | 0 | 0 | 0 | 0 | 0
207.5 | 0 | 0 | 0 | 0 | 0
208 | 0 | 0 | 0 | 0 | 0
208.5 | 0 | 0 | 0 | 0 | 0
209 | 0 | 0 | 0 | 0 | 0
209.5 | 0 | 0 | 0 | 0 | 0
210 | 0 | 0 | 0 | 0 | 0
210.5 | 0 | 0 | 0 | 0 | 0
211 | 0 | 0 | 0 | 0 | 0
211.5 | 0 | 0 | 0 | 0 | 0
212 | 0 | 0 | 0 | 0 | 0
212.5 | 0 | 0 | 0 | 0 | 0
213 | 0 | 0 | 0 | 0 | 0
213.5 | 0 | 0 | 0 | 0 | 0
214 | 0 | 0 | 0 | 0 | 0
214.5 | 0 | 0 | 0 | 0 | 0
215 | 0 | 0 | 0 | 0 | 0
215.5 | 0 | 0 | 0 | 0 | 0
216 | 0 | 0 | 0 | 0 | 0
216.5 | 0 | 0 | 0 | 0 | 0
217 | 0 | 0 | 0 | 0 | 0
217.5 | 0 | 0 | 0 | 0 | 0
218 | 0 | 0 | 0 | 0 | 0
218.5 | 0 | 0 | 0 | 0 | 0
219 | 0 | 0 | 0 | 0 | 0
219.5 | 0 | 0 | 0 | 0 | 0
220 | 0 | 0 | 0 | 0 | 0
220.5 | 0 | 0 | 0 | 0 | 0
221 | 0 | 0 | 0 | 0 | 0
221.5 | 0 | 0 | 0 | 0 | 0
222 | 0 | 0 | 0 | 0 | 0
222.5 | 0 | 0 | 0 | 0 | 0
223 | 0 | 0 | 0 | 0 | 0
223.5 | 0 | 0 | 0 | 0 | 0
224 | 0 | 0 | 0 | 0 | 0
224.5 | 0 | 0 | 0 | 0 | 0
225 | 0 | 0 | 0 | 0 | 0
225.5 | 0 | 0 | 0 | 0 | 0
226 | 0 | 0 | 0 | 0 | 0
226.5 | 0 | 0 | 0 | 0 | 0
227 | 0 | 0 | 0 | 0 | 0
227.5 | 0 | 0 | 0 | 0 | 0
228 | 0 | 0 | 0 | 0 | 0
228.5 | 0 | 0 | 0 | 0 | 0
229 | 0 | 0 | 0 | 0 | 0
229.5 | 0 | 0 | 0 | 0 | 0
230 | 0 | 0 | 0 | 0 | 0
230.5 | 0 | 0 | 0 | 0 | 0
231 | 0 | 0 | 0 | 0 | 0
231.5 | 0 | 0 | 0 | 0 | 0
232 | 0 | 0 | 0 | 0 | 0
232.5 | 0 | 0 | 0 | 0 | 0
233 | 0 | 0 | 0 | 0 | 0
233.5 | 0 | 0 | 0 | 0 | 0
234 | 0 | 0 | 0 | 0 | 0
234.5 | 0 | 0 | 0 | 0 | 0
235 | 0 | 0 | 0 | 0 | 0
235.5 | 0 | 0 | 0 | 0 | 0
236 | 0 | 0 | 0 | 0 | 0
236.5 | 0 | 0 | 0 | 0 | 0
237 | 0 | 0 | 0 | 0 | 0
237.5 | 0 | 0 | 0 | 0 | 0
238 | 0 | 0 | 0 | 0 | 0
238.5 | 0 | 0 | 0 | 0 | 0
239 | 0 | 0 | 0 | 0 | 0
239.5 | 0 | 0 | 0 | 0 | 0
240 | 0 | 0 | 0 | 0 | 0
240.5 | 0 | 0 | 0 | 0 | 0
241 | 0 | 0 | 0 | 0 | 0
241.5 | 0 | 0 | 0 | 0 | 0
242 | 0 | 0 | 0 | 0 | 0
242.5 | 0 | 0 | 0 | 0 | 0
243 | 0 | 0 | 0 | 0 | 0
243.5 | 0 | 0 | 0 | 0 | 0
244 | 0 | 0 | 0 | 0 | 0
244.5 | 0 | 0 | 0 | 0 | 0
245 | 0 | 0 | 0 | 0 | 0
245.5 | 0 | 0 | 0 | 0 | 0
246 | 0 | 0 | 0 | 0 | 0
246.5 | 0 | 0 | 0 | 0 | 0
247 | 0 | 0 | 0 | 0 | 0
247.5 | 0 | 0 | 0 | 0 | 0
248 | 0 | 0 | 0 | 0 | 0
248.5 | 0 | 0 | 0 | 0 | 0
249 | 0 | 0 | 0 | 0 | 0
249.5 | 0 | 0 | 0 | 0 | 0
250 | 0 | 0 | 0 | 0 | 0
250.5 | 0 | 0 | 0 | 0 | 0
251 | 0 | 0 | 0 | 0 | 0
251.5 | 0 | 0 | 0 | 0 | 0
252 | 0 | 0 | 0 | 0 | 0
252.5 | 0 | 0 | 0 | 0 | 0
253 | 0 | 0 | 0 | 0 | 0
253.5 | 0 | 0 | 0 | 0 | 0
254 | 0 | 0 | 0 | 0 | 0
254.5 | 0 | 0 | 0 | 0 | 0
255 | 0 | 0 | 0 | 0 | 0
255.5 | 0 | 0 | 0 | 0 | 0
256 | 0 | 0 | 0 | 0 | 0
256.5 | 0 | 0 | 0 | 0 | 0
257 | 0 | 0 | 0 | 0 | 0
257.5 | 0 | 0 | 0 | 0 | 0
258 | 0 | 0 | 0 | 0 | 0
258.5 | 0 | 0 | 0 | 0 | 0
259 | 0 | 0 | 0 | 0 | 0
259.5 | 0 | 0 | 0 | 0 | 0
260 | 0 | 0 | 0 | 0 | 0
260.5 | 0 | 0 | 0 | 0 | 0
261 | 0 | 0 | 0 | 0 | 0
261.5 | 0 | 0 | 0 | 0 | 0
262 | 0 | 0 | 0 | 0 | 0
262.5 | 0 | 0 | 0 | 0 | 0
263 | 0 | 0 | 0 | 0 | 0
263.5 | 0 | 0 | 0 | 0 | 0
264 | 0 | 0 | 0 | 0 | 0
264.5 | 0 | 0 | 0 | 0 | 0
265 | 0 | 0 | 0 | 0 | 0
265.5 | 0 | 0 | 0 | 0 | 0
266 | 0 | 0 | 0 | 0 | 0
266.5 | 0 | 0 | 0 | 0 | 0
267 | 0 | 0 | 0 | 0 | 0
267.5 | 0 | 0 | 0 | 0 | 0
268 | 0 | 0 | 0 | 0 | 0
268.5 | 0 | 0 | 0 | 0 | 0
269 | 0 | 0 | 0 | 0 | 0
269.5 | 0 | 0 | 0 | 0 | 0
270 | 0 | 0 | 0 | 0 | 0
270.5 | 0 | 0 | 0 | 0 | 0
271 | 0 | 0 | 0 | 0 | 0
271.5 | 0 | 0 | 0 | 0 | 0
272 | 0 | 0 | 0 | 0 | 0
272.5 | 0 | 0 | 0 | 0 | 0
273 | 0 | 0 | 0 | 0 | 0
273.5 | 0 | 0 | 0 | 0 | 0
274 | 0 | 0 | 0 | 0 | 0
274.5 | 0 | 0 | 0 | 0 | 0
275 | 0 | 0 | 0 | 0 | 0
275.5 | 0 | 0 | 0 | 0 | 0
276 | 0 | 0 | 0 | 0 | 0
276.5 | 0 | 0 | 0 | 0 | 0
277 | 0 | 0 | 0 | 0 | 0
277.5 | 0 | 0 | 0 | 0 | 0
278 | 0 | 0 | 0 | 0 | 0
278.5 | 0 | 0 | 0 | 0 | 0
279 | 0 | 0 | 0 | 0 | 0
279.5 | 0 | 0 | 0 | 0 | 0
280 | 0 | 0 | 0 | 0 | 0
280.5 | 0 | 0 | 0 | 0 | 0
281 | 0 | 0 | 0 | 0 | 0
281.5 | 0 | 0 | 0 | 0 | 0
282 | 0 | 0 | 0 | 0 | 0
282.5 | 0 | 0 | 0 | 0 | 0
283 | 0 | 0 | 0 | 0 | 0
283.5 | 0 | 0 | 0 | 0 | 0
284 | 0 | 0 | 0 | 0 | 0
284.5 | 0 | 0 | 0 | 0 | 0
285 | 0 | 0 | 0 | 0 | 0
285.5 | 0 | 0 | 0 | 0 | 0
286 | 0 | 0 | 0 | 0 | 0
286.5 | 0 | 0 | 0 | 0 | 0
287 | 0 | 0 | 0 | 0 | 0
287.5 | 0 | 0 | 0 | 0 | 0
288 | 0 | 0 | 0 | 0 | 0
288.5 | 0 | 0 | 0 | 0 | 0
289 | 0 | 0 | 0 | 0 | 0
289.5 | 0 | 0 | 0 | 0 | 0
290 | 0 | 0 | 0 | 0 | 0
290.5 | 0 | 0 | 0 | 0 | 0
291 | 0 | 0 | 0 | 0 | 0
291.5 | 0 | 0 | 0 | 0 | 0
292 | 0 | 0 | 0 | 0 | 0
292.5 | 0 | 0 | 0 | 0 | 0
293 | 0 | 0 | 0 | 0 | 0
293.5 | 0 | 0 | 0 | 0 | 0
294 | 0 | 0 | 0 | 0 | 0
294.5 | 0 | 0 | 0 | 0 | 0
295 | 0 | 0 | 0 | 0 | 0
295.5 | 0 | 0 | 0 | 0 | 0
296 | 0 | 0 | 0 | 0 | 0
296.5 | 0 | 0 | 0 | 0 | 0
297 | 0 | 0 | 0 | 0 | 0
297.5 | 0 | 0 | 0 | 0 | 0
298 | 0 | 0 | 0 | 0 | 0
298.5 | 0 | 0 | 0 | 0 | 0
299 | 0 | 0 | 0 | 0 | 0
299.5 | 0 | 0 | 0 | 0 | 0
300 | 0 | 0 | 0 | 0 | 0
300.5 | 0 | 0 | 0 | 0 | 0
301 | 0 | 0 | 0 | 0 | 0
301.5 | 0 | 0 | 0 | 0 | 0
302 | 0 | 0 | 0 | 0 | 0
302.5 | 0 | 0 | 0 | 0 | 0
303 | 0 | 0 | 0 | 0 | 0
303.5 | 0 | 0 | 0 | 0 | 0
304 | 0 | 0 | 0 | 0 | 0
304.5 | 0 | 0 | 0 | 0 | 0
305 | 0 | 0 | 0 | 0 | 0
305.5 | 0 | 0 | 0 | 0 | 0
306 | 0 | 0 | 0 | 0 | 0
306.5 | 0 | 0 | 0 | 0 | 0
307 | 0 | 0 | 0 | 0 | 0
307.5 | 0 | 0 | 0 | 0 | 0
308 | 0 | 0 | 0 | 0 | 0
308.5 | 0 | 0 | 0 | 0 | 0
309 | 0 | 0 | 0 | 0 | 0
309.5 | 0 | 0 | 0 | 0 | 0
310 | 0 | 0 | 0 | 0 | 0
310.5 | 0 | 0 | 0 | 0 | 0
311 | 0 | 0 | 0 | 0 | 0
311.5 | 0 | 0 | 0 | 0 | 0
312 | 0 | 0 | 0 | 0 | 0
312.5 | 0 | 0 | 0 | 0 | 0
313 | 0 | 0 | 0 | 0 | 0
313.5 | 0 | 0 | 0 | 0 | 0
314 | 0 | 0 | 0 | 0 | 0
314.5 | 0 | 0 | 0 | 0 | 0
315 | 0 | 0 | 0 | 0 | 0
315.5 | 0 | 0 | 0 | 0 | 0
316 | 0 | 0 | 0 | 0 | 0
316.5 | 0 | 0 | 0 | 0 | 0
317 | 0 | 0 | 0 | 0 | 0
317.5 | 0 | 0 | 0 | 0 | 0
318 | 0 | 0 | 0 | 0 | 0
318.5 | 0 | 0 | 0 | 0 | 0
319 | 0 | 0 | 0 | 0 | 0
319.5 | 0 | 0 | 0 | 0 | 0
320 | 0 | 0 | 0 | 0 | 0
320.5 | 0 | 0 | 0 | 0 | 0
321 | 0 | 0 | 0 | 0 | 0
321.5 | 0 | 0 | 0 | 0 | 0
322 | 0 | 0 | 0 | 0 | 0
322.5 | 0 | 0 | 0 | 0 | 0
323 | 0 | 0 | 0 | 0 | 0
323.5 | 0 | 0 | 0 | 0 | 0
324 | 0 | 0 | 0 | 0 | 0
324.5 | 0 | 0 | 0 | 0 | 0
325 | 0 | 0 | 0 | 0 | 0
325.5 | 0 | 0 | 0 | 0 | 0
326 | 0 | 0 | 0 | 0 | 0
326.5 | 0 | 0 | 0 | 0 | 0
327 | 0 | 0 | 0 | 0 | 0
327.5 | 0 | 0 | 0 | 0 | 0
328 | 0 | 0 | 0 | 0 | 0
328.5 | 0 | 0 | 0 | 0 | 0
329 | 0 | 0 | 0 | 0 | 0
329.5 | 0 | 0 | 0 | 0 | 0
330 | 0 | 0 | 0 | 0 | 0
330.5 | 0 | 0 | 0 | 0 | 0
331 | 0 | 0 | 0 | 0 | 0
331.5 | 0 | 0 | 0 | 0 | 0
332 | 0 | 0 | 0 | 0 | 0
332.5 | 0 | 0 | 0 | 0 | 0
333 | 0 | 0 | 0 | 0 | 0
333.5 | 0 | 0 | 0 | 0 | 0
334 | 0 | 0 | 0 | 0 | 0
334.5 | 0 | 0 | 0 | 0 | 0
335 | 0 | 0 | 0 | 0 | 0
335.5 | 0 | 0 | 0 | 0 | 0
336 | 0 | 0 | 0 | 0 | 0
336.5 | 0 | 0 | 0 | 0 | 0
337 | 0 | 0 | 0 | 0 | 0
337.5 | 0 | 0 | 0 | 0 | 0
338 | 0 | 0 | 0 | 0 | 0
338.5 | 0 | 0 | 0 | 0 | 0
339 | 0 | 0 | 0 | 0 | 0
339.5 | 0 | 0 | 0 | 0 | 0
340 | 0 | 0 | 0 | 0 | 0
340.5 | 0 | 0 | 0 | 0 | 0
341 | 0 | 0 | 0 | 0 | 0
341.5 | 0 | 0 | 0 | 0 | 0
342 | 0 | 0 | 0 | 0 | 0
342.5 | 0 | 0 | 0 | 0 | 0
343 | 0 | 0 | 0 | 0 | 0
343.5 | 0 | 0 | 0 | 0 | 0
344 | 0 | 0 | 0 | 0 | 0
344.5 | 0 | 0 | 0 | 0 | 0
345 | 0 | 0 | 0 | 0 | 0
345.5 | 0 | 0 | 0 | 0 | 0
346 | 0 | 0 | 0 | 0 | 0
346.5 | 0 | 0 | 0 | 0 | 0
347 | 0 | 0 | 0 | 0 | 0
347.5 | 0 | 0 | 0 | 0 | 0
348 | 0 | 0 | 0 | 0 | 0
348.5 | 0 | 0 | 0 | 0 | 0
349 | 0 | 0 | 0 | 0 | 0
349.5 | 0 | 0 | 0 | 0 | 0
350 | 0 | 0 | 0 | 0 | 0
350.5 | 0 | 0 | 0 | 0 | 0
351 | 0 | 0 | 0 | 0 | 0
351.5 | 0 | 0 | 0 | 0 | 0
352 | 0 | 0 | 0 | 0 | 0
352.5 | 0 | 0 | 0 | 0 | 0
353 | 0 | 0 | 0 | 0 | 0
353.5 | 0 | 0 | 0 | 0 | 0
354 | 0 | 0 | 0 | 0 | 0
354.5 | 0 | 0 | 0 | 0 | 0
355 | 0 | 0 | 0 | 0 | 0
355.5 | 0 | 0 | 0 | 0 | 0
356 | 0 | 0 | 0 | 0 | 0
356.5 | 0 | 0 | 0 | 0 | 0
357 | 0 | 0 | 0 | 0 | 0
357.5 | 0 | 0 | 0 | 0 | 0
358 | 0 | 0 | 0 | 0 | 0
358.5 | 0 | 0 | 0 | 0 | 0
359 | 0 | 0 | 0 | 0 | 0
359.5 | 0 | 0 | 0 | 0 | 0
360 | 0 | 0 | 0 | 0 | 0
360.5 | 0 | 0 | 0 | 0 | 0
361 | 0 | 0 | 0 | 0 | 0
361.5 | 0 | 0 | 0 | 0 | 0
362 | 0 | 0 | 0 | 0 | 0
362.5 | 0 | 0 | 0 | 0 | 0
363 | 0 | 0 | 0 | 0 | 0
363.5 | 0 | 0 | 0 | 0 | 0
364 | 0 | 0 | 0 | 0 | 0
364.5 | 0 | 0 | 0 | 0 | 0
365 | 0 | 0 | 0 | 0 | 0
365.5 | 0 | 0 | 0 | 0 | 0
366 | 0 | 0 | 0 | 0 | 0
366.5 | 0 | 0 | 0 | 0 | 0
367 | 0 | 0 | 0 | 0 | 0
367.5 | 0 | 0 | 0 | 0 | 0
368 | 0 | 0 | 0 | 0 | 0
368.5 | 0 | 0 | 0 | 0 | 0
369 | 0 | 0 | 0 | 0 | 0
369.5 | 0 | 0 | 0 | 0 | 0
370 | 0 | 0 | 0 | 0 | 0
370.5 | 0 | 0 | 0 | 0 | 0
371 | 0 | 0 | 0 | 0 | 0
371.5 | 0 | 0 | 0 | 0 | 0
372 | 0 | 0 | 0 | 0 | 0
372.5 | 0 | 0 | 0 | 0 | 0
373 | 0 | 0 | 0 | 0 | 0
373.5 | 0 | 0 | 0 | 0 | 0
374 | 0 | 0 | 0 | 0 | 0
374.5 | 0 | 0 | 0 | 0 | 0
375 | 0 | 0 | 0 | 0 | 0
375.5 | 0 | 0 | 0 | 0 | 0
376 | 0 | 0 | 0 | 0 | 0
376.5 | 0 | 0 | 0 | 0 | 0
377 | 0 | 0 | 0 | 0 | 0
377.5 | 0 | 0 | 0 | 0 | 0
378 | 0 | 0 | 0 | 0 | 0
378.5 | 0 | 0 | 0 | 0 | 0
379 | 0 | 0 | 0 | 0 | 0
379.5 | 0 | 0 | 0 | 0 | 0
380 | 0 | 0 | 0 | 0 | 0
380.5 | 0 | 0 | 0 | 0 | 0
381 | 0 | 0 | 0 | 0 | 0
381.5 | 0 | 0 | 0 | 0 | 0
382 | 0 | 0 | 0 | 0 | 0
382.5 | 0 | 0 | 0 | 0 | 0
383 | 0 | 0 | 0 | 0 | 0
383.5 | 0 | 0 | 0 | 0 | 0
384 | 0 | 0 | 0 | 0 | 0
384.5 | 0 | 0 | 0 | 0 | 0
385 | 0 | 0 | 0 | 0 | 0
385.5 | 0 | 0 | 0 | 0 | 0
386 | 0 | 0 | 0 | 0 | 0
386.5 | 0 | 0 | 0 | 0 | 0
387 | 0 | 0 | 0 | 0 | 0
387.5 | 0 | 0 | 0 | 0 | 0
388 | 0 | 0 | 0 | 0 | 0
388.5 | 0 | 0 | 0 | 0 | 0
389 | 0 | 0 | 0 | 0 | 0
389.5 | 0 | 0 | 0 | 0 | 0
390 | 0 | 0 | 0 | 0 | 0
390.5 | 0 | 0 | 0 | 0 | 0
391 | 0 | 0 | 0 | 0 | 0
391.5 | 0 | 0 | 0 | 0 | 0
392 | 0 | 0 | 0 | 0 | 0
392.5 | 0 | 0 | 0 | 0 | 0
393 | 0 | 0 | 0 | 0 | 0
393.5 | 0 | 0 | 0 | 0 | 0
394 | 0 | 0 | 0 | 0 | 0
394.5 | 0 | 0 | 0 | 0 | 0
395 | 0 | 0 | 0 | 0 | 0
395.5 | 0 | 0 | 0 | 0 | 0
396 | 0 | 0 | 0 | 0 | 0
396.5 | 0 | 0 | 0 | 0 | 0
397 | 0 | 0 | 0 | 0 | 0
397.5 | 0 | 0 | 0 | 0 | 0
398 | 0 | 0 | 0 | 0 | 0
398.5 | 0 | 0 | 0 | 0 | 0
399 | 0 | 0 | 0 | 0 | 0
399.5 | 0 | 0 | 0 | 0 | 0
400 | 0 | 0 | 0 | 0 | 0
400.5 | 0 | 0 | 0 | 0 | 0
401 | 0 | 0 | 0 | 0 | 0
401.5 | 0 | 0 | 0 | 0 | 0
402 | 0 | 0 | 0 | 0 | 0
402.5 | 0 | 0 | 0 | 0 | 0
403 | 0 | 0 | 0 | 0 | 0
403.5 | 0 | 0 | 0 | 0 | 0
404 | 0 | 0 | 0 | 0 | 0
404.5 | 0 | 0 | 0 | 0 | 0
405 | 0 | 0 | 0 | 0 | 0
405.5 | 0 | 0 | 0 | 0 | 0
406 | 0 | 0 | 0 | 0 | 0
406.5 | 0 | 0 | 0 | 0 | 0
407 | 0 | 0 | 0 | 0 | 0
407.5 | 0 | 0 | 0 | 0 | 0
408 | 0 | 0 | 0 | 0 | 0
408.5 | 0 | 0 | 0 | 0 | 0
409 | 0 | 0 | 0 | 0 | 0
409.5 | 0 | 0 | 0 | 0 | 0
410 | 0 | 0 | 0 | 0 | 0
410.5 | 0 | 0 | 0 | 0 | 0
411 | 0 | 0 | 0 | 0 | 0
411.5 | 0 | 0 | 0 | 0 | 0
412 | 0 | 0 | 0 | 0 | 0
412.5 | 0 | 0 | 0 | 0 | 0
413 | 0 | 0 | 0 | 0 | 0
413.5 | 0 | 0 | 0 | 0 | 0
414 | 0 | 0 | 0 | 0 | 0
414.5 | 0 | 0 | 0 | 0 | 0
415 | 0 | 0 | 0 | 0 | 0
415.5 | 0 | 0 | 0 | 0 | 0
416 | 0 | 0 | 0 | 0 | 0
416.5 | 0 | 0 | 0 | 0 | 0
417 | 0 | 0 | 0 | 0 | 0
417.5 | 0 | 0 | 0 | 0 | 0
418 | 0 | 0 | 0 | 0 | 0
418.5 | 0 | 0 | 0 | 0 | 0
419 | 0 | 0 | 0 | 0 | 0
419.5 | 0 | 0 | 0 | 0 | 0
420 | 0 | 0 | 0 | 0 | 0
420.5 | 0 | 0 | 0 | 0 | 0
421 | 0 | 0 | 0 | 0 | 0
421.5 | 0 | 0 | 0 | 0 | 0
422 | 0 | 0 | 0 | 0 | 0
422.5 | 0 | 0 | 0 | 0 | 0
423 | 0 | 0 | 0 | 0 | 0
423.5 | 0 | 0 | 0 | 0 | 0
424 | 0 | 0 | 0 | 0 | 0
424.5 | 0 | 0 | 0 | 0 | 0
425 | 0 | 0 | 0 | 0 | 0
425.5 | 0 | 0 | 0 | 0 | 0
426 | 0 | 0 | 0 | 0 | 0
426.5 | 0 | 0 | 0 | 0 | 0
427 | 0 | 0 | 0 | 0 | 0
427.5 | 0 | 0 | 0 | 0 | 0
428 | 0 | 0 | 0 | 0 | 0
428.5 | 0 | 0 | 0 | 0 | 0
429 | 0 | 0 | 0 | 0 | 0
429.5 | 0 | 0 | 0 | 0 | 0
430 | 0 | 0 | 0 | 0 | 0
430.5 | 0 | 0 | 0 | 0 | 0
431 | 0 | 0 | 0 | 0 | 0
431.5 | 0 | 0 | 0 | 0 | 0
432 | 0 | 0 | 0 | 0 | 0
432.5 | 0 | 0 | 0 | 0 | 0
433 | 0 | 0 | 0 | 0 | 0
433.5 | 0 | 0 | 0 | 0 | 0
434 | 0 | 0 | 0 | 0 | 0
434.5 | 0 | 0 | 0 | 0 | 0
435 | 0 | 0 | 0 | 0 | 0
435.5 | 0 | 0 | 0 | 0 | 0
436 | 0 | 0 | 0 | 0 | 0
436.5 | 0 | 0 | 0 | 0 | 0
437 | 0 | 0 | 0 | 0 | 0
437.5 | 0 | 0 | 0 | 0 | 0
438 | 0 | 0 | 0 | 0 | 0
438.5 | 0 | 0 | 0 | 0 | 0
439 | 0 | 0 | 0 | 0 | 0
439.5 | 0 | 0 | 0 | 0 | 0
440 | 0 | 0 | 0 | 0 | 0
440.5 | 0 | 0 | 0 | 0 | 0
441 | 0 | 0 | 0 | 0 | 0
441.5 | 0 | 0 | 0 | 0 | 0
442 | 0 | 0 | 0 | 0 | 0
442.5 | 0 | 0 | 0 | 0 | 0
443 | 0 | 0 | 0 | 0 | 0
443.5 | 0 | 0 | 0 | 0 | 0
444 | 0 | 0 | 0 | 0 | 0
444.5 | 0 | 0 | 0 | 0 | 0
445 | 0 | 0 | 0 | 0 | 0
445.5 | 0 | 0 | 0 | 0 | 0
446 | 0 | 0 | 0 | 0 | 0
446.5 | 0 | 0 | 0 | 0 | 0
447 | 0 | 0 | 0 | 0 | 0
447.5 | 0 | 0 | 0 | 0 | 0
448 | 0 | 0 | 0 | 0 | 0
448.5 | 0 | 0 | 0 | 0 | 0
449 | 0 | 0 | 0 | 0 | 0
449.5 | 0 | 0 | 0 | 0 | 0
450 | 0 | 0 | 0 | 0 | 0
450.5 | 0 | 0 | 0 | 0 | 0
451 | 0 | 0 | 0 | 0 | 0
451.5 | 0 | 0 | 0 | 0 | 0
452 | 0 | 0 | 0 | 0 | 0
452.5 | 0 | 0 | 0 | 0 | 0
453 | 0 | 0 | 0 | 0 | 0
453.5 | 0 | 0 | 0 | 0 | 0
454 | 0 | 0 | 0 | 0 | 0
454.5 | 0 | 0 | 0 | 0 | 0
455 | 0 | 0 | 0 | 0 | 0
455.5 | 0 | 0 | 0 | 0 | 0
456 | 0 | 0 | 0 | 0 | 0
456.5 | 0 | 0 | 0 | 0 | 0
457 | 0 | 0 | 0 | 0 | 0
457.5 | 0 | 0 | 0 | 0 | 0
458 | 0 | 0 | 0 | 0 | 0
458.5 | 0 | 0 | 0 | 0 | 0
459 | 0 | 0 | 0 | 0 | 0
459.5 | 0 | 0 | 0 | 0 | 0
460 | 0 | 0 | 0 | 0 | 0
460.5 | 0 | 0 | 0 | 0 | 0
461 | 0 | 0 | 0 | 0 | 0
461.5 | 0 | 0 | 0 | 0 | 0
462 | 0 | 0 | 0 | 0 | 0
462.5 | 0 | 0 | 0 | 0 | 0
463 | 0 | 0 | 0 | 0 | 0
463.5 | 0 | 0 | 0 | 0 | 0
464 | 0 | 0 | 0 | 0 | 0
464.5 | 0 | 0 | 0 | 0 | 0
465 | 0 | 0 | 0 | 0 | 0
465.5 | 0 | 0 | 0 | 0 | 0
466 | 0 | 0 | 0 | 0 | 0
466.5 | 0 | 0 | 0 | 0 | 0
467 | 0 | 0 | 0 | 0 | 0
467.5 | 0 | 0 | 0 | 0 | 0
468 | 0 | 0 | 0 | 0 | 0
468.5 | 0 | 0 | 0 | 0 | 0
469 | 0 | 0 | 0 | 0 | 0
469.5 | 0 | 0 | 0 | 0 | 0
470 | 0 | 0 | 0 | 0 | 0
470.5 | 0 | 0 | 0 | 0 | 0
471 | 0 | 0 | 0 | 0 | 0
471.5 | 0 | 0 | 0 | 0 | 0
472 | 0 | 0 | 0 | 0 | 0
472.5 | 0 | 0 | 0 | 0 | 0
473 | 0 | 0 | 0 | 0 | 0
473.5 | 0 | 0 | 0 | 0 | 0
474 | 0 | 0 | 0 | 0 | 0
474.5 | 0 | 0 | 0 | 0 | 0
475 | 0 | 0 | 0 | 0 | 0
475.5 | 0 | 0 | 0 | 0 | 0
476 | 0 | 0 | 0 | 0 | 0
476.5 | 0 | 0 | 0 | 0 | 0
477 | 0 | 0 | 0 | 0 | 0
477.5 | 0 | 0 | 0 | 0 | 0
478 | 0 | 0 | 0 | 0 | 0
478.5 | 0 | 0 | 0 | 0 | 0
479 | 0 | 0 | 0 | 0 | 0
479.5 | 0 | 0 | 0 | 0 | 0
480 | 0 | 0 | 0 | 0 | 0
480.5 | 0 | 0 | 0 | 0 | 0
481 | 0 | 0 | 0 | 0 | 0
481.5 | 0 | 0 | 0 | 0 | 0
482 | 0 | 0 | 0 | 0 | 0
482.5 | 0 | 0 | 0 | 0 | 0
483 | 0 | 0 | 0 | 0 | 0
483.5 | 0 | 0 | 0 | 0 | 0
484 | 0 | 0 | 0 | 0 | 0
484.5 | 0 | 0 | 0 | 0 | 0
485 | 0 | 0 | 0 | 0 | 0
485.5 | 0 | 0 | 0 | 0 | 0
486 | 0 | 0 | 0 | 0 | 0
486.5 | 0 | 0 | 0 | 0 | 0
487 | 0 | 0 | 0 | 0 | 0
487.5 | 0 | 0 | 0 | 0 | 0
488 | 0 | 0 | 0 | 0 | 0
488.5 | 0 | 0 | 0 | 0 | 0
489 | 0 | 0 | 0 | 0 | 0
489.5 | 0 | 0 | 0 | 0 | 0
490 | 0 | 0 | 0 | 0 | 0
490.5 | 0 | 0 | 0 | 0 | 0
491 | 0 | 0 | 0 | 0 | 0
491.5 | 0 | 0 | 0 | 0 | 0
492 | 0 | 0 | 0 | 0 | 0
492.5 | 0 | 0 | 0 | 0 | 0
493 | 0 | 0 | 0 | 0 | 0
493.5 | 0 | 0 | 0 | 0 | 0
494 | 0 | 0 | 0 | 0 | 0
494.5 | 0 | 0 | 0 | 0 | 0
495 | 0 | 0 | 0 | 0 | 0
495.5 | 0 | 0 | 0 | 0 | 0
496 | 0 | 0 | 0 | 0 | 0
496.5 | 0 | 0 | 0 | 0 | 0
497 | 0 | 0 | 0 | 0 | 0
497.5 | 0 | 0 | 0 | 0 | 0
498 | 0 | 0 | 0 | 0 | 0
498.5 | 0 | 0 | 0 | 0 | 0
499 | 0 | 0 | 0 | 0 | 0
499.5 | 0 | 0 | 0 | 0 | 0
500 | 0 | 0 | 0 | 0 | 0
500.5 | 0 | 0 | 0 | 0 | 0
501 | 0 | 0 | 0 | 0 | 0
501.5 | 0 | 0 | 0 | 0 | 0
502 | 0 | 0 | 0 | 0 | 0
502.5 | 0 | 0 | 0 | 0 | 0
503 | 0 | 0 | 0 | 0 | 0
503.5 | 0 | 0 | 0 | 0 | 0
504 | 0 | 0 | 0 | 0 | 0
504.5 | 0 | 0 | 0 | 0 | 0
505 | 0 | 0 | 0 | 0 | 0
505.5 | 0 | 0 | 0 | 0 | 0
506 | 0 | 0 | 0 | 0 | 0
506.5 | 0 | 0 | 0 | 0 | 0
507 | 0 | 0 | 0 | 0 | 0
507.5 | 0 | 0 | 0 | 0 | 0
508 | 0 | 0 | 0 | 0 | 0
508.5 | 0 | 0 | 0 | 0 | 0
509 | 0 | 0 | 0 | 0 | 0
509.5 | 0 | 0 | 0 | 0 | 0
510 | 0 | 0 | 0 | 0 | 0
510.5 | 0 | 0 | 0 | 0 | 0
511 | 0 | 0 | 0 | 0 | 0
511.5 | 0 | 0 | 0 | 0 | 0
512 | 0 | 0 | 0 | 0 | 0
512.5 | 0 | 0 | 0 | 0 | 0
513 | 0 | 0 | 0 | 0 | 0
513.5 | 0 | 0 | 0 | 0 | 0
514 | 0 | 0 | 0 | 0 | 0
514.5 | 0 | 0 | 0 | 0 | 0
515 | 0 | 0 | 0 | 0 | 0
515.5 | 0 | 0 | 0 | 0 | 0
516 | 0 | 0 | 0 | 0 | 0
516.5 | 0 | 0 | 0 | 0 | 0
517 | 0 | 0 | 0 | 0 | 0
517.5 | 0 | 0 | 0 | 0 | 0
518 | 0 | 0 | 0 | 0 | 0
518.5 | 0 | 0 | 0 | 0 | 0
519 | 0 | 0 | 0 | 0 | 0
519.5 | 0 | 0 | 0 | 0 | 0
520 | 0 | 0 | 0 | 0 | 0
520.5 | 0 | 0 | 0 | 0 | 0
521 | 0 | 0 | 0 | 0 | 0
521.5 | 0 | 0 | 0 | 0 | 0
522 | 0 | 0 | 0 | 0 | 0
522.5 | 0 | 0 | 0 | 0 | 0
523 | 0 | 0 | 0 | 0 | 0
523.5 | 0 | 0 | 0 | 0 | 0
524 | 0 | 0 | 0 | 0 | 0
524.5 | 0 | 0 | 0 | 0 | 0
525 | 0 | 0 | 0 | 0 | 0
525.5 | 0 | 0 | 0 | 0 | 0
526 | 0 | 0 | 0 | 0 | 0
526.5 | 0 | 0 | 0 | 0 | 0
527 | 0 | 0 | 0 | 0 | 0
527.5 | 0 | 0 | 0 | 0 | 0
528 | 0 | 0 | 0 | 0 | 0
528.5 | 0 | 0 | 0 | 0 | 0
529 | 0 | 0 | 0 | 0 | 0
529.5 | 0 | 0 | 0 | 0 | 0
530 | 0 | 0 | 0 | 0 | 0
530.5 | 0 | 0 | 0 | 0 | 0
531 | 0 | 0 | 0 | 0 | 0
531.5 | 0 | 0 | 0 | 0 | 0
532 | 0 | 0 | 0 | 0 | 0
532.5 | 0 | 0 | 0 | 0 | 0
533 | 0 | 0 | 0 | 0 | 0
533.5 | 0 | 0 | 0 | 0 | 0
534 | 0 | 0 | 0 | 0 | 0
534.5 | 0 | 0 | 0 | 0 | 0
535 | 0 | 0 | 0 | 0 | 0
535.5 | 0 | 0 | 0 | 0 | 0
536 | 0 | 0 | 0 | 0 | 0
536.5 | 0 | 0 | 0 | 0 | 0
537 | 0 | 0 | 0 | 0 | 0
537.5 | 0 | 0 | 0 | 0 | 0
538 | 0 | 0 | 0 | 0 | 0
538.5 | 0 | 0 | 0 | 0 | 0
539 | 0 | 0 | 0 | 0 | 0
539.5 | 0 | 0 | 0 | 0 | 0
540 | 0 | 0 | 0 | 0 | 0
540.5 | 0 | 0 | 0 | 0 | 0
541 | 0 | 0 | 0 | 0 | 0
541.5 | 0 | 0 | 0 | 0 | 0
542 | 0 | 0 | 0 | 0 | 0
542.5 | 0 | 0 | 0 | 0 | 0
543 | 0 | 0 | 0 | 0 | 0
543.5 | 0 | 0 | 0 | 0 | 0
544 | 0 | 0 | 0 | 0 | 0
544.5 | 0 | 0 | 0 | 0 | 0
545 | 0 | 0 | 0 | 0 | 0
545.5 | 0 | 0 | 0 | 0 | 0
546 | 0 | 0 | 0 | 0 | 0
546.5 | 0 | 0 | 0 | 0 | 0
547 | 0 | 0 | 0 | 0 | 0
547.5 | 0 | 0 | 0 | 0 | 0
548 | 0 | 0 | 0 | 0 | 0