## CaseRodEject_in
# CaseRodEject -- Control Rod Ejection Accident with Nordheim-Fuchs burst model.
# Rod worth: 750 pcm in 0.05 s. beta_eff = 650 pcm, so delta_rho = 100 pcm
# above prompt critical. The NF model is activated when rho_net > beta_eff.
#
# Physics sequence:
# 0-0.04 s: rho_ext < 650 pcm; PJA applies at each 0.01 s step.
# 0.05 s: rho_ext = 750 pcm > 650 pcm; NF sub-integration fires.
# Power spikes on the prompt neutron timescale (ms), then
# self-terminates via adiabatic Doppler feedback.
# Trip detected during NF burst; scram fires 1.5 s later.
# Post-scram: decay heat cooling; full recovery.
#
# Initial power: 10 MW (hot zero power) so absolute temperatures are
# manageable while still clearly demonstrating the NF dynamics.
# PORV at 16500 kPa prevents pressure termination during burst.
# T_fuel_limit_C = 3000 prevents premature cladding termination.
# Job Control
endtime = 100
# RCS Geometry
R5_lowCV_height = 70 * 0.3048
R5_highCV_height = 7 * 0.3048
R5_area = 33.0 * 0.3048**2
loop_vol_m3 = 5.0
# Accumulator and ECCS
acc_area = 66.63 * 0.3048**2
acc_length = 10.5 * 0.3048
acc_totvol = acc_area * acc_length
acc_gasvol = acc_totvol - 630.0 * 0.3048**3
acc_narea = 0.032 * 0.3048**2
inflow_info = {'pressure': 101.0, 'temp': 49.85}
# Initial Conditions
pressure_kPa = 14820.0
pressure_containment = 101.0
temp_core_exit = 285.0 # HZP: coolant near secondary saturation
# Break Model
diameter_break = 0.0
Cd_sub = 0.93
Cd_sat = 0.93
Slip_model = "Fauske"
transition_mixture_mass = 0.463
# ADV / PORV
setpoint_ADV_open = 16500.0
area_per_ADV = 0.01266
ADV_number = 0
PORV_setpoint_kPa = 16500 # prevents overpressure termination
PORV_area_m2 = 0.005
# Reactor Power and Decay Heat
total_power = 575
Tinf = 365 * 24 * 3600
U239yield = 1.0
fr35 = 0.81
fr38 = 0.13
fr39 = 0.06
Efis = 200
# Simulation Flags
pump_flag = 1
sg_flag = 1
core_flag = 1
dnbr_flag = 1
full_power_flag = 0
pump_scram_trip = 1
# RPS Trips
trip_P_lo_kPa = 0
trip_P_hi_kPa = 0
trip_power_frac = 1.10
trip_time_s = 1e6
trip_flow_frac = 0
# Core Heat Transfer
F_r = 1.3
F_z = 1.55
k_fuel = 3.0
h_gap = 6000.0
r_fuel_m = 0.00418
rho_fuel = 10400.0
cp_fuel = 330.0
htc_relax = 0.3
T_fuel_limit_C = 3000 # allow NF burst without premature termination
# Point Kinetics -- Nordheim-Fuchs rod ejection
ria_flag = 1
initial_power_MW = 10.0 # HZP: 10 MW starting condition
alpha_D_pcm = -3.0
alpha_M_pcm = -35.0
Lambda_star = 0.083
high_flux_trip = 1.10
beta_eff_pcm = 650.0
pja_flag = 1 # PJA for sub-critical phase
Lambda_prompt = 5e-5 # prompt neutron lifetime [s] for NF model
nf_H_active_m = 2.44 # active fuel height for C_f [m]
Time (s) | Structure Q (MW) | Decay Heat (MW) | Steam Generator (MW) | # Deprecated | rho_ext (pcm)
0 | 0 | 0 | 0 | 0 | 0
0.005 | 0 | 0 | 0 | 0 | 75
0.01 | 0 | 0 | 0 | 0 | 150
0.015 | 0 | 0 | 0 | 0 | 225
0.02 | 0 | 0 | 0 | 0 | 300
0.025 | 0 | 0 | 0 | 0 | 375
0.03 | 0 | 0 | 0 | 0 | 450
0.035 | 0 | 0 | 0 | 0 | 525
0.04 | 0 | 0 | 0 | 0 | 600
0.045 | 0 | 0 | 0 | 0 | 675
0.05 | 0 | 0 | 0 | 0 | 750
0.5 | 0 | 0 | 0 | 0 | 750
1 | 0 | 0 | 0 | 0 | 750
1.5 | 0 | 0 | 0 | 0 | 750
2 | 0 | 0 | 0 | 0 | 750
2.5 | 0 | 0 | 0 | 0 | 750
3 | 0 | 0 | 0 | 0 | 750
3.5 | 0 | 0 | 0 | 0 | 750
4 | 0 | 0 | 0 | 0 | 750
4.5 | 0 | 0 | 0 | 0 | 750
5 | 0 | 0 | 0 | 0 | 750
5.5 | 0 | 0 | 0 | 0 | 750
6 | 0 | 0 | 0 | 0 | 750
6.5 | 0 | 0 | 0 | 0 | 750
7 | 0 | 0 | 0 | 0 | 750
7.5 | 0 | 0 | 0 | 0 | 750
8 | 0 | 0 | 0 | 0 | 750
8.5 | 0 | 0 | 0 | 0 | 750
9 | 0 | 0 | 0 | 0 | 750
9.5 | 0 | 0 | 0 | 0 | 750
10 | 0 | 0 | 0 | 0 | 750
10.5 | 0 | 0 | 0 | 0 | 750
11 | 0 | 0 | 0 | 0 | 750
11.5 | 0 | 0 | 0 | 0 | 750
12 | 0 | 0 | 0 | 0 | 750
12.5 | 0 | 0 | 0 | 0 | 750
13 | 0 | 0 | 0 | 0 | 750
13.5 | 0 | 0 | 0 | 0 | 750
14 | 0 | 0 | 0 | 0 | 750
14.5 | 0 | 0 | 0 | 0 | 750
15 | 0 | 0 | 0 | 0 | 750
15.5 | 0 | 0 | 0 | 0 | 750
16 | 0 | 0 | 0 | 0 | 750
16.5 | 0 | 0 | 0 | 0 | 750
17 | 0 | 0 | 0 | 0 | 750
17.5 | 0 | 0 | 0 | 0 | 750
18 | 0 | 0 | 0 | 0 | 750
18.5 | 0 | 0 | 0 | 0 | 750
19 | 0 | 0 | 0 | 0 | 750
19.5 | 0 | 0 | 0 | 0 | 750
20 | 0 | 0 | 0 | 0 | 750
20.5 | 0 | 0 | 0 | 0 | 750
21 | 0 | 0 | 0 | 0 | 750
21.5 | 0 | 0 | 0 | 0 | 750
22 | 0 | 0 | 0 | 0 | 750
22.5 | 0 | 0 | 0 | 0 | 750
23 | 0 | 0 | 0 | 0 | 750
23.5 | 0 | 0 | 0 | 0 | 750
24 | 0 | 0 | 0 | 0 | 750
24.5 | 0 | 0 | 0 | 0 | 750
25 | 0 | 0 | 0 | 0 | 750
25.5 | 0 | 0 | 0 | 0 | 750
26 | 0 | 0 | 0 | 0 | 750
26.5 | 0 | 0 | 0 | 0 | 750
27 | 0 | 0 | 0 | 0 | 750
27.5 | 0 | 0 | 0 | 0 | 750
28 | 0 | 0 | 0 | 0 | 750
28.5 | 0 | 0 | 0 | 0 | 750
29 | 0 | 0 | 0 | 0 | 750
29.5 | 0 | 0 | 0 | 0 | 750
30 | 0 | 0 | 0 | 0 | 750
30.5 | 0 | 0 | 0 | 0 | 750
31 | 0 | 0 | 0 | 0 | 750
31.5 | 0 | 0 | 0 | 0 | 750
32 | 0 | 0 | 0 | 0 | 750
32.5 | 0 | 0 | 0 | 0 | 750
33 | 0 | 0 | 0 | 0 | 750
33.5 | 0 | 0 | 0 | 0 | 750
34 | 0 | 0 | 0 | 0 | 750
34.5 | 0 | 0 | 0 | 0 | 750
35 | 0 | 0 | 0 | 0 | 750
35.5 | 0 | 0 | 0 | 0 | 750
36 | 0 | 0 | 0 | 0 | 750
36.5 | 0 | 0 | 0 | 0 | 750
37 | 0 | 0 | 0 | 0 | 750
37.5 | 0 | 0 | 0 | 0 | 750
38 | 0 | 0 | 0 | 0 | 750
38.5 | 0 | 0 | 0 | 0 | 750
39 | 0 | 0 | 0 | 0 | 750
39.5 | 0 | 0 | 0 | 0 | 750
40 | 0 | 0 | 0 | 0 | 750
40.5 | 0 | 0 | 0 | 0 | 750
41 | 0 | 0 | 0 | 0 | 750
41.5 | 0 | 0 | 0 | 0 | 750
42 | 0 | 0 | 0 | 0 | 750
42.5 | 0 | 0 | 0 | 0 | 750
43 | 0 | 0 | 0 | 0 | 750
43.5 | 0 | 0 | 0 | 0 | 750
44 | 0 | 0 | 0 | 0 | 750
44.5 | 0 | 0 | 0 | 0 | 750
45 | 0 | 0 | 0 | 0 | 750
45.5 | 0 | 0 | 0 | 0 | 750
46 | 0 | 0 | 0 | 0 | 750
46.5 | 0 | 0 | 0 | 0 | 750
47 | 0 | 0 | 0 | 0 | 750
47.5 | 0 | 0 | 0 | 0 | 750
48 | 0 | 0 | 0 | 0 | 750
48.5 | 0 | 0 | 0 | 0 | 750
49 | 0 | 0 | 0 | 0 | 750
49.5 | 0 | 0 | 0 | 0 | 750
50 | 0 | 0 | 0 | 0 | 750
50.5 | 0 | 0 | 0 | 0 | 750
51 | 0 | 0 | 0 | 0 | 750
51.5 | 0 | 0 | 0 | 0 | 750
52 | 0 | 0 | 0 | 0 | 750
52.5 | 0 | 0 | 0 | 0 | 750
53 | 0 | 0 | 0 | 0 | 750
53.5 | 0 | 0 | 0 | 0 | 750
54 | 0 | 0 | 0 | 0 | 750
54.5 | 0 | 0 | 0 | 0 | 750
55 | 0 | 0 | 0 | 0 | 750
55.5 | 0 | 0 | 0 | 0 | 750
56 | 0 | 0 | 0 | 0 | 750
56.5 | 0 | 0 | 0 | 0 | 750
57 | 0 | 0 | 0 | 0 | 750
57.5 | 0 | 0 | 0 | 0 | 750
58 | 0 | 0 | 0 | 0 | 750
58.5 | 0 | 0 | 0 | 0 | 750
59 | 0 | 0 | 0 | 0 | 750
59.5 | 0 | 0 | 0 | 0 | 750
60 | 0 | 0 | 0 | 0 | 750
60.5 | 0 | 0 | 0 | 0 | 750
61 | 0 | 0 | 0 | 0 | 750
61.5 | 0 | 0 | 0 | 0 | 750
62 | 0 | 0 | 0 | 0 | 750
62.5 | 0 | 0 | 0 | 0 | 750
63 | 0 | 0 | 0 | 0 | 750
63.5 | 0 | 0 | 0 | 0 | 750
64 | 0 | 0 | 0 | 0 | 750
64.5 | 0 | 0 | 0 | 0 | 750
65 | 0 | 0 | 0 | 0 | 750
65.5 | 0 | 0 | 0 | 0 | 750
66 | 0 | 0 | 0 | 0 | 750
66.5 | 0 | 0 | 0 | 0 | 750
67 | 0 | 0 | 0 | 0 | 750
67.5 | 0 | 0 | 0 | 0 | 750
68 | 0 | 0 | 0 | 0 | 750
68.5 | 0 | 0 | 0 | 0 | 750
69 | 0 | 0 | 0 | 0 | 750
69.5 | 0 | 0 | 0 | 0 | 750
70 | 0 | 0 | 0 | 0 | 750
70.5 | 0 | 0 | 0 | 0 | 750
71 | 0 | 0 | 0 | 0 | 750
71.5 | 0 | 0 | 0 | 0 | 750
72 | 0 | 0 | 0 | 0 | 750
72.5 | 0 | 0 | 0 | 0 | 750
73 | 0 | 0 | 0 | 0 | 750
73.5 | 0 | 0 | 0 | 0 | 750
74 | 0 | 0 | 0 | 0 | 750
74.5 | 0 | 0 | 0 | 0 | 750
75 | 0 | 0 | 0 | 0 | 750
75.5 | 0 | 0 | 0 | 0 | 750
76 | 0 | 0 | 0 | 0 | 750
76.5 | 0 | 0 | 0 | 0 | 750
77 | 0 | 0 | 0 | 0 | 750
77.5 | 0 | 0 | 0 | 0 | 750
78 | 0 | 0 | 0 | 0 | 750
78.5 | 0 | 0 | 0 | 0 | 750
79 | 0 | 0 | 0 | 0 | 750
79.5 | 0 | 0 | 0 | 0 | 750
80 | 0 | 0 | 0 | 0 | 750
80.5 | 0 | 0 | 0 | 0 | 750
81 | 0 | 0 | 0 | 0 | 750
81.5 | 0 | 0 | 0 | 0 | 750
82 | 0 | 0 | 0 | 0 | 750
82.5 | 0 | 0 | 0 | 0 | 750
83 | 0 | 0 | 0 | 0 | 750
83.5 | 0 | 0 | 0 | 0 | 750
84 | 0 | 0 | 0 | 0 | 750
84.5 | 0 | 0 | 0 | 0 | 750
85 | 0 | 0 | 0 | 0 | 750
85.5 | 0 | 0 | 0 | 0 | 750
86 | 0 | 0 | 0 | 0 | 750
86.5 | 0 | 0 | 0 | 0 | 750
87 | 0 | 0 | 0 | 0 | 750
87.5 | 0 | 0 | 0 | 0 | 750
88 | 0 | 0 | 0 | 0 | 750
88.5 | 0 | 0 | 0 | 0 | 750
89 | 0 | 0 | 0 | 0 | 750
89.5 | 0 | 0 | 0 | 0 | 750
90 | 0 | 0 | 0 | 0 | 750
90.5 | 0 | 0 | 0 | 0 | 750
91 | 0 | 0 | 0 | 0 | 750
91.5 | 0 | 0 | 0 | 0 | 750
92 | 0 | 0 | 0 | 0 | 750
92.5 | 0 | 0 | 0 | 0 | 750
93 | 0 | 0 | 0 | 0 | 750
93.5 | 0 | 0 | 0 | 0 | 750
94 | 0 | 0 | 0 | 0 | 750
94.5 | 0 | 0 | 0 | 0 | 750
95 | 0 | 0 | 0 | 0 | 750
95.5 | 0 | 0 | 0 | 0 | 750
96 | 0 | 0 | 0 | 0 | 750
96.5 | 0 | 0 | 0 | 0 | 750
97 | 0 | 0 | 0 | 0 | 750
97.5 | 0 | 0 | 0 | 0 | 750
98 | 0 | 0 | 0 | 0 | 750
98.5 | 0 | 0 | 0 | 0 | 750
99 | 0 | 0 | 0 | 0 | 750
99.5 | 0 | 0 | 0 | 0 | 750
100 | 0 | 0 | 0 | 0 | 750