## CR6604_Case7_in
# NUREG/CR-6604 Case 7 — integrated 300-second LBLOCA
# Ordinary integrated FLARE; prescribed AST dose calculation continues to 2 hours.
# Edit column B. Column A updates to show FLARE assignments.
# TH surrogate from supplied four-loop LBLOCA; not a published Case 7 TH specification.
#
FLARE assignment | Value (editable) | Units | Meaning |  | Reference
# Plant and inventory |  |  |  |  | NUREG/CR-6604 §3.3.11, pp319–320
# |  |  |  |  | https://digital.library.unt.edu/ark:/67531/metadc695823/
plant_design = 'westinghouse_4_loop' | westinghouse_4_loop |  | Fuel geometry database selection
total_power = 1932. | 1932 | MWt | Analysis thermal power
nbt_inventory_model = 'yield_buildup' | yield_buildup |  | Analytical U-235 yield inventory, three equal batches; updated simulator/runtime isotope data required.
nbt_burnup_gwdmtu = 33. | 33 | GWd/MTU | Oldest batch burnup; three equal batches at 11, 22, 33 GWd/MTU. Core mean 22 GWd/MTU. Existing four-loop fuel-loading proxy retained.
nbt_calibrate = 1. | 1 |  | Dose multiplier; retain1 for comparison
# Source release phases
nbt_gap_release_duration_hr = 0.5 | 0.5 | h | Gap phase begins at shutdown and ends at 0.5 h.
nbt_early_iv_duration_hr = 1.3 | 1.3 | h | Early in-vessel phase 0.5–1.8 h.
#
# Decay and removal controls
nbt_credit_decay = False | FALSE |  | Group-average radioactive decay
nbt_sprays_on = False | FALSE |  | Spray removal credit
# Containment and EAB exposure
nbt_containment_volume_ft3 = 1730000. | 1730000 | ft³ | Single well-mixed containment
nbt_leak_rate_frac_per_day = 0.0012 | 0.0012 | fraction/day | 0.12%/day, not0.0012%/day
nbt_chi_q_eab = 0.001 | 0.001 | s/m³ | Constant0–2h; zero thereafter
nbt_breathing_rate_m3_s = 0.000347 | 0.000347 | m³/s | First-two-hour breathing rate
nbt_eab_integration_hr = 2. | 2 | h | Exposure stops at2h; no later EAB exposure
# Reference result
reference_eab_rem = 25.3 | 25.3 | rem | Published Case7 EAB TEDE
#
#
# Model notes
# Integrated LBLOCA below is a surrogate; Case 7 specifies radiological transport only.
# westinghouse_4_loop is the reference geometry used for normalization, not an identification of the original1932-MWt plant.
# Corrected inventories are power-scaled. Fuel geometry cancels from the normalized group activity.
# EAB benchmark only; LPZ and control-room outputs have no benchmark acceptance basis here.
# Target: nominal FLARE EAB 25.7135 rem; published Case 7 reference 25.3 rem.
#
#
#
#
#
#
#
#
# Integrated TH settings: supplied four-loop LBLOCA surrogate
R5_area = 15.165248141909007 | 15.1652 | m² | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
R5_lowCV_height = 6.096 | 6.096 | m | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
R5_highCV_height = 3.048 | 3.048 | m | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
loop_vol_m3 = 234 | 234 | m³ | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pzr_height = 16.1 | 16.1 | m | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pzr_level_init = 10.465000000000002 | 10.465 | m | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pzr_level_hi = 14.490000000000002 | 14.49 | m | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
acc_totvol = 147.264 | 147.264 | m³ | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
acc_gasvol = 45.312000000000005 | 45.312 | m³ | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
acc_area = 24.7605182208 | 24.7605 | m² | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
acc_length = 5.947533031691207 | 5.9475 | m | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
acc_narea = 0.01189158912 | 0.011892 | m² | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pressure_kPa = 15513 | 15513 | kPa | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
temp_core_exit = 324.7 | 324.7 | °C | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
fr35 = 0.81 | 0.81 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
fr38 = 0.13 | 0.13 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
fr39 = 0.06 | 0.06 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
F_r = 1.65 | 1.65 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
F_z = 1.55 | 1.55 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
Cd_sub = 0.93 | 0.93 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
Cd_sat = 0.93 | 0.93 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
transition_mixture_mass = 0.463 | 0.463 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
PORV_setpoint_kPa = 15990 | 15990 | kPa | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
PORV_area_m2 = 0.036 | 0.036 | m² | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
P_relax = 0.4 | 0.4 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
p_si_setpoint_Pa = 11700000 | 11700000 | Pa | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
hpsi_mdot_rated = 160 | 160 | kg/s | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
hpsi_p_shutoff_Pa = 12500000 | 12500000 | Pa | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
hpsi_p_rated_Pa = 4000000 | 4000000 | Pa | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
hpsi_delay_s = 25 | 25 | s | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
lpsi_mdot_rated = 350 | 350 | kg/s | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
lpsi_delay_s = 35 | 35 | s | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
rwst_mass_initial = 9000000 | 9000000 | kg | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
trip_rod_insertion_time_s = 2 | 2 | s | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
rcs_enthalpy_relax_tau_s = 25 | 25 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
endtime = 300 | 300 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
diameter_break = 0.6985 | 0.6985 |  | 27.5-inch single equivalent opening from supplied four-loop LBLOCA.
post_chf_model = 'cold_leg' | cold_leg |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
htc_post_chf = 450 | 450 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
film_boiling_level_m = 4 | 4 | m | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
dry_core_trigger_level_m = 2 | 2 | m | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
source_term_model = 'RG1183_LOCA' | RG1183_LOCA |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pump_rated_flow_m3s = 27.204 | 27.204 | m³/s | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pump_rated_head_m = 82.3 | 82.3 | m | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pump_rated_torque_Nm = 56063.6 | 56063.6 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pump_rated_density_kg_m3 = 720 | 720 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pump_inertia_kg_m2 = 129.357 | 129.357 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pump_flow_area_m2 = 2.1988 | 2.1988 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pump_friction_torque_Nm = 226.476 | 226.476 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
pump_friction_speed2_Nm = 226.476 | 226.476 |  | Supplied four-loop LBLOCA TH surrogate; not Case 7 report data.
break_elevation_m = 5.2 | 5.2 | m | Cold-leg elevation surrogate.
t_break = 0 | 0 | s | Break opens at start.
full_power_flag = 0 | 0 |  | Automatic protection enabled.
trip_time_s = 0 | 0 | s | Reactor trip at break initiation.
trip_delay = 0 | 0 | s | No added detection delay; rod ramp remains 2 s.
pump_trip_time = 0 | 0 | s | RCP trip and modeled coastdown.
si_enabled = True | TRUE |  | Enable accumulator, HPSI and LPSI.
lpsi_p_shutoff_Pa = 1500000 | 1500000 | Pa | Generic four-loop LPSI curve.
lpsi_p_rated_Pa = 300000 | 300000 | Pa | Generic four-loop LPSI curve.
nbt_credit_deposition = False | FALSE |  | Case 7: no natural removal.
nbt_filtered_leak_fraction = 0 | 0 |  | Case 7: no filtered leakage path.
nbt_end_time_hr = 2 | 2 | h | Independent dose calculation endpoint.
nbt_eab_search_end_hr = 2 | 2 | h | Case 7 EAB exposure ends at 2 h; restrict search accordingly.
nbt_distance_lpz_m = 4000 | 4000 | m | Unbenchmarked screening output only.
nbt_distance_eab_m = 914 | 914 | m | Unbenchmarked screening output only.
nbt_lpz_integration_hr = 720 | 720 | h | Unbenchmarked screening output only.
# | Structure Q (MW) | Decay Heat (MW) | SG Q (MW) | SI Flow (kg/s) | Reactivity (pcm)
Time (s) | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
1 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0
300

## Release Fractions
Group source release fractions
Fractions of core inventory. Each phase releases uniformly over its duration.
NBT group | Gap fraction | Early in-vessel fraction | Meaning
NG | 5% | 95% | Noble gases
Halogens | 5% | 35% | Iodine chemical forms set on input sheet
Alkali_metals | 5% | 25% | Cesium/rubidium group
Te_group | 0% | 5% | Tellurium group
Ba_Sr | 0% | 2% | Barium/strontium
Noble_metals | 0% | 0.25% | Corrected early in-vessel fraction0.0025
Ce_group | 0% | 0.05% | Cerium group
Lanthanides | 0% | 0.02% | Corrected early in-vessel fraction0.0002
U_actinides | 0% | 0.02% | No represented U-group inventory in reference60 dataset
NUREG/CR-6604 §3.3.11, pp319–320